## Fiber Fill Calculator
Fiber Optic Conduit Fill Calculator
For flat-drop, figure-8/messenger, and round fiber cable in conduit or innerduct.
1. Select Conduit / Innerduct
Conduit (type & trade size) | PVC Schedule 40 — 1"
Conduit internal area (100%), sq in | 0.832
Max fill basis | Flat 40% (typical telecom/innerduct guideline)
Custom fill % (only used if basis = Custom) | 40%
2. Enter Fiber Cables
Pick a cable from the library, or choose "Custom (enter shape & dimensions at right)" and fill in the orange cells with the exact cross-section from your cable's datasheet — flat-drop dimensions vary by manufacturer and fiber count, so "Custom" is the most reliable option.
# | Cable (from library or Custom) | Shape (if Custom) | Dim 1 - width/dia (in) | Dim 2 - height (in) | Quantity | Unit Area (sq in) | Total Area (sq in)
1 | Flat Drop, 2F, approx. 2.0mm x 5.0mm (example) |  |  |  | 4 | 0.012223 | 0.048893
2 | Custom (enter shape & dimensions at right) | Flat / Oval (elliptical) | 0.2 | 0.35 | 2 | 0.054978 | 0.10996
3
4
5
6
7
8
9
10
11
12
13
14
Totals |  |  |  |  | 6 |  | 0.15885
3. Results
Total number of cables |  | 6
Max fill allowed (%) |  | 40%
Conduit internal area, 100% (sq in) |  | 0.832
Maximum allowed fill area (sq in) |  | 0.3328
Total cable fill area (sq in) |  | 0.15885
Actual fill (% of conduit area) |  | 19.09%
Remaining capacity (sq in) |  | 0.17395
Status |  | PASS - within allowed fill
Note: rows below are examples using library entries. Replace with your own cables. For flat-drop cable, "Custom" with datasheet dimensions is more accurate than the library estimates.

## Conduit Data
Label | Conduit / Innerduct Type | Trade Size | Internal Area, 100% (sq in)
EMT — 1/2" | EMT | 1/2" | 0.304
EMT — 3/4" | EMT | 3/4" | 0.533
EMT — 1" | EMT | 1" | 0.864
EMT — 1-1/4" | EMT | 1-1/4" | 1.496
EMT — 1-1/2" | EMT | 1-1/2" | 2.036
EMT — 2" | EMT | 2" | 3.356
EMT — 2-1/2" | EMT | 2-1/2" | 5.858
EMT — 3" | EMT | 3" | 8.846
EMT — 3-1/2" | EMT | 3-1/2" | 11.545
EMT — 4" | EMT | 4" | 14.753
ENT — 1/2" | ENT | 1/2" | 0.285
ENT — 3/4" | ENT | 3/4" | 0.508
ENT — 1" | ENT | 1" | 0.832
ENT — 1-1/4" | ENT | 1-1/4" | 1.453
ENT — 1-1/2" | ENT | 1-1/2" | 1.986
ENT — 2" | ENT | 2" | 3.291
RMC — 1/2" | RMC | 1/2" | 0.314
RMC — 3/4" | RMC | 3/4" | 0.549
RMC — 1" | RMC | 1" | 0.887
RMC — 1-1/4" | RMC | 1-1/4" | 1.526
RMC — 1-1/2" | RMC | 1-1/2" | 2.071
RMC — 2" | RMC | 2" | 3.408
RMC — 2-1/2" | RMC | 2-1/2" | 4.866
RMC — 3" | RMC | 3" | 7.499
RMC — 3-1/2" | RMC | 3-1/2" | 10.01
RMC — 4" | RMC | 4" | 12.882
RMC — 5" | RMC | 5" | 20.212
RMC — 6" | RMC | 6" | 29.158
PVC Schedule 40 — 1/2" | PVC Schedule 40 | 1/2" | 0.285
PVC Schedule 40 — 3/4" | PVC Schedule 40 | 3/4" | 0.508
PVC Schedule 40 — 1" | PVC Schedule 40 | 1" | 0.832
PVC Schedule 40 — 1-1/4" | PVC Schedule 40 | 1-1/4" | 1.453
PVC Schedule 40 — 1-1/2" | PVC Schedule 40 | 1-1/2" | 1.986
PVC Schedule 40 — 2" | PVC Schedule 40 | 2" | 3.291
PVC Schedule 40 — 2-1/2" | PVC Schedule 40 | 2-1/2" | 4.695
PVC Schedule 40 — 3" | PVC Schedule 40 | 3" | 7.268
PVC Schedule 40 — 3-1/2" | PVC Schedule 40 | 3-1/2" | 9.737
PVC Schedule 40 — 4" | PVC Schedule 40 | 4" | 12.554
PVC Schedule 40 — 5" | PVC Schedule 40 | 5" | 19.761
PVC Schedule 40 — 6" | PVC Schedule 40 | 6" | 28.567
PVC Schedule 80 — 1/2" | PVC Schedule 80 | 1/2" | 0.217
PVC Schedule 80 — 3/4" | PVC Schedule 80 | 3/4" | 0.409
PVC Schedule 80 — 1" | PVC Schedule 80 | 1" | 0.688
PVC Schedule 80 — 1-1/4" | PVC Schedule 80 | 1-1/4" | 1.237
PVC Schedule 80 — 1-1/2" | PVC Schedule 80 | 1-1/2" | 1.711
PVC Schedule 80 — 2" | PVC Schedule 80 | 2" | 2.874
PVC Schedule 80 — 2-1/2" | PVC Schedule 80 | 2-1/2" | 4.119
PVC Schedule 80 — 3" | PVC Schedule 80 | 3" | 6.442
PVC Schedule 80 — 3-1/2" | PVC Schedule 80 | 3-1/2" | 8.688
PVC Schedule 80 — 4" | PVC Schedule 80 | 4" | 11.258
PVC Schedule 80 — 5" | PVC Schedule 80 | 5" | 17.855
PVC Schedule 80 — 6" | PVC Schedule 80 | 6" | 25.598
HDPE Conduit/Innerduct, SDR 11 (typical) — 3/4" | HDPE Conduit/Innerduct, SDR 11 (typical) | 3/4" | 0.24
HDPE Conduit/Innerduct, SDR 11 (typical) — 1" | HDPE Conduit/Innerduct, SDR 11 (typical) | 1" | 0.442
HDPE Conduit/Innerduct, SDR 11 (typical) — 1-1/4" | HDPE Conduit/Innerduct, SDR 11 (typical) | 1-1/4" | 0.694
HDPE Conduit/Innerduct, SDR 11 (typical) — 1-1/2" | HDPE Conduit/Innerduct, SDR 11 (typical) | 1-1/2" | 0.985
HDPE Conduit/Innerduct, SDR 11 (typical) — 2" | HDPE Conduit/Innerduct, SDR 11 (typical) | 2" | 1.744
HDPE Conduit/Innerduct, SDR 13.5 (typical) — 3/4" | HDPE Conduit/Innerduct, SDR 13.5 (typical) | 3/4" | 0.267
HDPE Conduit/Innerduct, SDR 13.5 (typical) — 1" | HDPE Conduit/Innerduct, SDR 13.5 (typical) | 1" | 0.487
HDPE Conduit/Innerduct, SDR 13.5 (typical) — 1-1/4" | HDPE Conduit/Innerduct, SDR 13.5 (typical) | 1-1/4" | 0.762
HDPE Conduit/Innerduct, SDR 13.5 (typical) — 1-1/2" | HDPE Conduit/Innerduct, SDR 13.5 (typical) | 1-1/2" | 1.081
HDPE Conduit/Innerduct, SDR 13.5 (typical) — 2" | HDPE Conduit/Innerduct, SDR 13.5 (typical) | 2" | 1.909
EMT / ENT / RMC / PVC Schedule 40 & 80: NEC Chapter 9, Table 4 (2020 NEC) — commonly published reference figures. Verify against the current NEC edition and local amendments.
HDPE conduit/innerduct rows are TYPICAL/EXAMPLE inside-diameter areas only — actual ID varies by manufacturer and SDR/wall-thickness rating. Confirm the true ID from your conduit's spec sheet and edit these rows (or add new ones) before relying on the result.

## Fiber Cable Library
Label | Shape | Dim 1 - width/dia (in) | Dim 2 - height (in) | Area (sq in)
Flat Drop, 2F, approx. 2.0mm x 5.0mm (example) | Flat / Oval (elliptical) | 0.079 | 0.197 | 0.012223
Flat Drop, 4F, approx. 2.0mm x 5.8mm (example) | Flat / Oval (elliptical) | 0.079 | 0.228 | 0.014147
Flat Drop, 6-8F, approx. 2.5mm x 6.5mm (example) | Flat / Oval (elliptical) | 0.098 | 0.256 | 0.019704
Flat Drop, 12F, approx. 3.0mm x 8.0mm (example) | Flat / Oval (elliptical) | 0.118 | 0.315 | 0.029193
Round Self-Support Drop (fig-8), approx. 5.0-8.0mm od (example) | Round | 0.256 |  | 0.051472
Round Simplex Drop, approx. 3.0mm od (example) | Round | 0.118 |  | 0.010936
Round Micro Drop, approx. 2.0mm od (example) | Round | 0.079 |  | 0.0049017
Custom (enter shape & dimensions at right) | Enter on main tab
EXAMPLE DIMENSIONS ONLY. Flat-drop and drop-cable cross sections vary significantly by manufacturer and fiber count and are NOT standardized like copper conductor tables. These rows are illustrative starting points; always confirm exact width x height (or diameter) from the specific cable's datasheet, and edit or add rows here — or use "Custom (enter shape & dimensions at right)" on the main tab — with the real dimensions before relying on this calculator.
Flat/oval cross sections are approximated as an ellipse (Area = pi x (width/2) x (height/2)). This is a reasonable industry approximation for a rounded flat-drop jacket; for a more conservative (larger) estimate, use the "Flat (rectangular estimate)" shape option instead, which uses Area = width x height.

## Instructions
How to use this workbook
1. Select conduit/innerduct
On the "Fiber Fill Calculator" tab, choose the conduit or innerduct type and trade size from the yellow dropdown in cell C6.
2. Choose a fill basis
Cell C8 sets the maximum allowed fill percentage: the NEC Chapter 9, Table 1 curve (53% for 1 cable, 31% for 2, 40% for 3+, the same ratios used for electrical conductors), a flat 40% (a common telecom/innerduct rule of thumb), or a Custom % you set in C9 (e.g. some innerduct manufacturers or project specs call for a different max, such as 50-60% for cell-type innerduct).
3. List cables
In the yellow/orange table, pick each cable from the library dropdown, or select "Custom (enter shape & dimensions at right)" and fill in the orange Shape/Dim 1/Dim 2 cells yourself using the exact cross-section from the cable's datasheet. Enter the quantity of that cable. Two example rows are pre-filled — replace them with your own cables and clear unused rows.
4. Read results
The Results section shows total cable fill area, the maximum area allowed, the actual fill percentage, remaining capacity, and a PASS/FAIL status.
5. Adjust as needed
If the status is FAIL, remove/relocate cables or choose a larger conduit/innerduct in C6 until the status reads PASS.
Why fiber is different from copper conductor fill
NEC Chapter 9, Table 5 gives standardized cross-sectional areas for round copper building-wire conductors by AWG/kcmil size. Fiber drop cable has no equivalent standardized table: flat-drop jackets are non-round and their dimensions are set by each manufacturer and fiber count. This workbook therefore lets you enter the real width x height (or diameter) directly, and approximates a flat/oval jacket as an ellipse (or, conservatively, a rectangle).
Reference data
The "Conduit Data" tab holds conduit/innerduct internal areas (NEC Chapter 9, Table 4 for standard electrical conduit; typical example figures for HDPE innerduct — verify against your product's spec sheet). The "Fiber Cable Library" tab holds example flat-drop and round drop cable dimensions — replace these with your actual cable's datasheet dimensions for an accurate result.
Important
Always confirm conduit/innerduct internal dimensions and cable cross-section dimensions from manufacturer datasheets, and confirm the fill percentage your project/authority having jurisdiction requires, before relying on this calculation for an actual installation.